{"text_format":"1","workbook":"xlsx","n_sheets":3,"sheets":["Пресметки","Сијалици","Светилки"],"not_rendered":{"charts":0,"images":8,"macros":1,"external_links":0,"defined_names":3,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Пресметки","index":0,"n_rows":38,"n_cols":11,"rows_kept":38,"cut":false,"hidden":false,"merged":[[16,1,16,3],[5,1,5,2],[28,5,28,7],[29,6,29,7],[0,0,21,0],[22,0,27,0],[28,0,38,0],[1,2,1,8],[32,1,32,2],[11,1,11,2],[3,5,3,8]]}
["1 чекор"]
[null,"Опис на просторијата","Проба"]
[]
[null,"Средна осветленост",500,"lx",null,"Коефициенти на рефлексија"]
[null,null,null,null,null,"Плафон",{"$f":"$H$8*I5/100","v":70},"%",70]
[null,"Димензии на просторијата",null,null,null,"Ѕидови",{"$f":"$H$8*I6/100","v":50},"%",50]
[null,"b=",20,"m",null,"Работна рамнина",{"$f":"$H$8*I7/100","v":10},"%",10]
[null,"a=",28,"m",null,null,"Коефициент на нечистотија на просторијата",100,"%"]
[null,"h=",4.5,"m"]
[null,"Површина",{"$f":"C7*C8","v":560},"m2","k=",{"$f":"C7*C8/C15/(C8+C7)","v":3.1963470319634708}]
[]
[null,"Висини",null,null,null,"Сијалица","ФС 36/840"]
[null,"h3=",0.85,"m",null,"Флукс",3350,"lm"]
[null,"h2=",0,"m",null,"Светилка"," I 0115 436"]
[null,"h1=",{"$f":"IF(ABS(C9)-ABS(C13)-ABS(C14)>0,ABS(C9)-ABS(C13)-ABS(C14),\"Грешка\")","v":3.65},"m",null,"Сијалици","4x36W"]
[null,null,null,null,null,"CIE Flux Codes","62 94 100 100 64"]
[null,"Коефициенти",null,null,null,"Сијалици во светилка",4]
[null,"Стареење",87,"%",null,"Флукс на светилка",13400,"lm"]
[null,"Преживување",100,"%",null,"Должина на светилката",0.59700000286102295,"m"]
[null,"Нечистотија на светилки",83,"%",null,"Ширина на светилката",1.1970000267028809,"m"]
[null,"MF",{"$f":"C18*C19*C20/100^2","v":72.209999999999994},"%"]
[]
["2 чекор",null,null,null,null,"Плафон:",60.144813537597656,"lx"]
[null,"Приближен број светилки","6x8=48",null,null,"Ѕидови:",175.50312805175781,"lx"]
[null,"nB",6,null,null,"Работна рамнина:",508.77984619140625,"lx",{"$f":"IF(G25*$C$4>0,1-$C$4/G25,0)","v":1.7256670556292431E-2}]
[null,"nA",8,null,null,"Работна рамнина дир. комп.:",455.11764526367188,"lx"]
[null,"Осветленост (раб. рамн.)",508.77984619140625,"lx"]
[]
["3 чекор",null,null,null,null,"РЕЗУЛТАТИ"]
[null,"Усвоен број светилки",{"$f":"C31*C32","v":48},null,"max",null,"Осветленост"]
[null,"nB=",6,null,{"$f":"nmax(B31,$C$38,G19,G20,C8,C7)","v":16},"Плафон=",60.144813537597656,"lx"]
[null,"nA=",8,null,{"$f":"nmax(B32,$C$38,G19,G20,C8,C7)","v":46},"Ѕидови=",175.50312805175781,"lx"]
[null,"Позиции на светилките",null,null,"c'=c/2","Работна рамнина=",508.77984619140625,"lx",{"$f":"IF(G33*$C$4>0,1-$C$4/G33,0)","v":1.7256670556292431E-2},"eta=",{"$f":"G33*C10/(C21*C30*G18/100)","v":0.61344346735713551}]
[null,"x0=",1.6666666269302368,"m",{"$f":"IF(C31>0,C7/C31/2,\"\")","v":1.6666666666666667}]
[null,"y0=",1.75,"m",{"$f":"IF(C32>0,C8/C32/2,\"\")","v":1.75},"Работна рамнина дир. комп.=",455.11764526367188,"lx"]
[null,"c=",3.3333332538604736,"m",{"$f":"IF(ABS(C38-0)<0.01,G19,G20)","v":1.1970000267028809}]
[null,"d=",3.5,"m",{"$f":"IF(ABS(C38-0)<0.01,G20,G19)","v":0.59700000286102295},"c/h1=",{"$f":"C36/C15","v":0.91324198735903395}]
[null,"Ротација",90,"˚",null,"sqrt(a*b/nsv)/h1=",{"$f":"IF(C30*C15>0,SQRT(C8*C7/C30)/C15,\"\")","v":0.93579459049859348}]

{"sheet":"Сијалици","index":1,"n_rows":50,"n_cols":5,"rows_kept":50,"cut":false,"hidden":false,"merged":[]}
["Тип на сијалица","Моќност (W)","Флукс (lm)","CCT (K)","Ra"]
["ФС 18/730",18,1150,3000,2]
["ФС 18/830",18,1350,3000,"1B"]
["ФС 18/930",18,940,3000,"1A"]
["ФС 18/740",18,1150,4000,2]
["ФС 18/840",18,1350,4000,"1B"]
["ФС 18/940",18,1000,4000,"1A"]
["ФС 18/765",18,1050,6500,2]
["ФС 18/865",18,1300,6500,"1B"]
["ФС 18/965",18,870,6500,"1A"]
["ФС 36/730",36,2700,3000,2]
["ФС 36/830",36,3350,3000,"1B"]
["ФС 36/930",36,2250,3000,"1A"]
["ФС 36/735",36,2800,3500,2]
["ФС 36/740",36,2850,4000,2]
["ФС 36/743",36,2700,4000,2]
["ФС 36/840",36,3350,4000,"1B"]
["ФС 36/843",36,3250,4000,"1B"]
["ФС 36/940",36,2400,4300,"1A"]
["ФС 36/765",36,2500,6500,2]
["ФС 36/865",36,3250,6500,"1B"]
["ФС 36/965",36,2100,6500,"1A"]
["ФС 58/730",58,4600,3000,2]
["ФС 58/735",58,4600,3500,2]
["ФС 58/830",58,5200,3000,"1B"]
["ФС 58/930",58,3650,3000,"1A"]
["ФС 58/740",58,4600,4000,2]
["ФС 58/840",58,5200,4000,"1B"]
["ФС 58/940",58,3850,4000,"1A"]
["ФС 58/765",58,4000,6500,2]
["ФС 58/865",58,5000,6500,"1B"]
["ФС 58/965",58,3350,6500,"1A"]
["ЖС(HQL) 125/634",125,6700,3400,2]
["ЖС(HQL) 125/642",125,6700,4100,2]
["ЖС(HQL) 125/534",125,5900,3400,3]
["ЖС(HQL) 125/542",125,5900,4100,3]
["ЖС(HQL) 250/534",250,13500,3400,3]
["ЖС(HQL) 250/542",250,12700,4100,3]
["ЖС(HQL) 400/534",400,23400,3500,3]
["ЖС(HQL) 400/542",400,22000,3900,3]
["НСВП(NAV) 70/220",70,5900,1900,4]
["НСВП(NAV) 250/220",250,31300,2000,4]
["НСВП(NAV) 250/621",250,22000,2150,2]
["НСВП(NAV) 400/220",400,55400,1900,4]
["НСВП(NAV) 400/621",400,37000,2150,2]
["MХС(HQI) 250/745",250,18000,4500,2]
["MХС(HQI) 250/640",250,20500,4000,2]
["MХС(HQI) 250/737",250,19000,3600,2]
["MХС(HQI) 400/745",400,32500,4400,2]
["MХС(HQI) 400/637",400,33400,3700,2]

{"sheet":"Светилки","index":2,"n_rows":344,"n_cols":10,"rows_kept":344,"cut":false,"hidden":false,"merged":[]}
["Тип на светилка","N1","N2","N3","N4","N5","Број на сијалици","Моќност на сијалицата (W)","Должина (m)","Ширина (m)"]
["Д 01 218",38,68,88,76,63,2,18,0.66,0.3]
["Д 01 236",38,68,88,76,63,2,36,1.27,0.3]
["Д 01 258",38,68,88,76,63,2,58,1.57,0.3]
["Д 02 318",39,69,89,79,56,3,18,0.66,0.45]
["Д 02 336",39,69,89,79,56,3,36,1.27,0.45]
["Д 02 358",39,69,89,79,56,3,58,1.57,0.45]
["Д 03 218",61,89,98,98,50,2,18,0.66,0.3]
["Д 03 236",61,89,98,98,50,2,36,1.27,0.3]
["Д 03 258",61,89,98,98,50,2,58,1.57,0.3]
["Д 04 318",60,89,98,100,55,3,18,0.66,0.45]
["Д 04 336",60,89,98,100,55,3,36,1.27,0.45]
["Д 04 358",60,89,98,100,55,3,58,1.57,0.45]
["Д 05 218",67,95,99,100,60,2,18,0.66,0.3]
["Д 05 236",67,95,99,100,60,2,36,1.27,0.3]
["Д 05 258",67,95,99,100,60,2,58,1.57,0.3]
["Д 05 318",67,95,99,100,60,3,18,0.66,0.45]
["Д 05 336",67,95,99,100,60,3,36,1.27,0.45]
["Д 05 358",67,95,99,100,60,3,58,1.57,0.45]
["Д 05 418",67,95,99,100,60,4,18,0.66,0.6]
["Д 05 436",67,95,99,100,60,4,36,1.27,0.6]
["Д 05 458",67,95,99,100,60,4,58,1.57,0.6]
["Д 07 218",45,77,95,95,43,2,18,0.6,0.6]
["Д 07 236",45,77,95,95,43,2,36,1.2,0.6]
["Д 05 258",45,77,95,95,43,2,58,1.5,0.6]
["Д 08 318",44,75,93,91,52,3,18,0.6,0.6]
["Д 08 336",44,75,93,91,52,3,36,12,0.6]
["Д 08 358",44,75,93,91,52,3,58,1.5,0.6]
["Д 09 218",65,91,98,100,42,2,18,0.6,0.6]
["Д 09 236",65,91,98,100,42,2,36,1.2,0.6]
["Д 09 258",65,91,98,100,42,2,58,1.5,0.6]
["Д 10 218",69,94,99,100,52,2,18,0.6,0.6]
["Д 10 236",69,94,99,100,52,2,36,1.2,0.6]
["Д 10 258",69,94,99,100,52,2,58,1.5,0.6]
["Д 11 218",34,62,85,60,96,2,18,0.62,0.2]
["Д 11 236",34,62,85,60,96,2,36,1.23,0.2]
["Д 11 258",34,62,85,60,96,2,58,1.53,0.2]
["Д 12 318",35,65,88,60,94,3,18,0.62,0.3]
["Д 12 336",35,65,88,60,94,3,36,1.23,0.3]
["Д 12 358",35,65,88,60,94,3,58,1.53,0.3]
["Д 13 218",44,76,95,100,82,2,18,0.62,0.25]
["Д 13 236",44,76,95,100,82,2,36,1.23,0.25]
["Д 13 258",44,76,95,100,82,2,58,1.53,0.25]
["Д 14 318",43,76,95,100,81,3,18,0.62,0.35]
["Д 14 336",43,76,95,100,81,3,36,1.23,0.35]
["Д 14 358",43,76,95,100,81,3,58,1.53,0.35]
["Д 15 236",34,63,86,59,85,2,36,1.36,0.3]
["Д 16 236",39,68,89,79,93,2,36,1.26,0.3]
["Д 17 1400",43,76,96,100,87,1,400,0.3,0.3]
["Д 18 1125",58,89,99,100,79,1,125,0.4,0.4]
[" I 0111 218",83,100,100,100,61,2,18,0.29699999999999999,0.59699999999999998]
[" I 0111 236",83,100,100,100,61,2,36,0.29699999999999999,1.1970000000000001]
[" I 0111 258",83,100,100,100,61,2,58,0.29699999999999999,1.4970000000000001]
[" I 0111 318",81,100,100,100,67,3,18,0.59699999999999998,0.59699999999999998]
[" I 0111 336",81,100,100,100,67,3,36,0.59699999999999998,1.1970000000000001]
[" I 0111 418",81,100,100,100,67,4,18,0.59699999999999998,0.59699999999999998]
[" I 0111 436",81,100,100,100,67,4,36,0.59699999999999998,1.1970000000000001]
[" I 0112 218",90,100,100,100,57,2,18,0.29699999999999999,0.59699999999999998]
[" I 0112 236",90,100,100,100,57,2,36,0.29699999999999999,1.1970000000000001]
[" I 0112 258",90,100,100,100,57,2,58,0.29699999999999999,1.4970000000000001]
[" I 0112 318",87,100,100,100,87,3,18,0.59699999999999998,0.59699999999999998]
[" I 0112 336",87,100,100,100,87,3,36,0.59699999999999998,1.1970000000000001]
[" I 0112 418",87,100,100,100,87,4,18,0.59699999999999998,0.59699999999999998]
[" I 0112 436",87,100,100,100,87,4,36,0.59699999999999998,1.1970000000000001]
[" I 0114 218",65,95,100,100,57,2,18,0.29699999999999999,0.59699999999999998]
[" I 0114 236",65,95,100,100,57,2,36,0.29699999999999999,1.1970000000000001]
[" I 0114 258",65,95,100,100,57,2,58,0.29699999999999999,1.4970000000000001]
[" I 0114 318",70,100,100,100,64,3,18,0.59699999999999998,0.59699999999999998]
[" I 0114 336",70,100,100,100,64,3,36,0.59699999999999998,1.1970000000000001]
[" I 0114 418",70,100,100,100,64,4,18,0.59699999999999998,0.59699999999999998]
[" I 0114 436",70,100,100,100,64,4,36,0.59699999999999998,1.1970000000000001]
[" I 0115 218",70,100,100,100,42,2,18,0.29699999999999999,0.59699999999999998]
[" I 0115 236",70,100,100,100,42,2,36,0.29699999999999999,1.1970000000000001]
[" I 0115 258",70,100,100,100,42,2,58,0.29699999999999999,1.4970000000000001]
[" I 0115 318",62,94,100,100,64,3,18,0.59699999999999998,0.59699999999999998]
[" I 0115 336",62,94,100,100,64,3,36,0.59699999999999998,1.1970000000000001]
[" I 0115 418",62,94,100,100,64,4,18,0.59699999999999998,0.59699999999999998]
[" I 0115 436",62,94,100,100,64,4,36,0.59699999999999998,1.1970000000000001]
[" I 0116 218",44,76,97,100,59,2,18,0.29699999999999999,0.59699999999999998]
[" I 0116 236",44,76,97,100,59,2,36,0.29699999999999999,1.1970000000000001]
[" I 0116 258",44,76,97,100,59,2,58,0.29699999999999999,1.4970000000000001]
[" I 0116 318",44,76,97,100,59,3,18,0.59699999999999998,0.59699999999999998]
[" I 0116 336",44,76,97,100,59,3,36,0.59699999999999998,1.1970000000000001]
[" I 0116 418",44,76,97,100,59,4,18,0.59699999999999998,0.59699999999999998]
[" I 0116 436",44,76,97,100,59,4,36,0.59699999999999998,1.1970000000000001]
[" I 0117 218",51,81,98,100,58,2,18,0.29699999999999999,0.59699999999999998]
[" I 0117 236",51,81,98,100,58,2,36,0.29699999999999999,1.1970000000000001]
[" I 0117 258",51,81,98,100,58,2,58,0.29699999999999999,1.4970000000000001]
[" I 0117 318",52,82,98,100,66,3,18,0.59699999999999998,0.59699999999999998]
[" I 0117 336",52,82,98,100,66,3,36,0.59699999999999998,1.1970000000000001]
[" I 0117 418",52,82,98,100,66,4,18,0.59699999999999998,0.59699999999999998]
[" I 0117 436",52,82,98,100,66,4,36,0.59699999999999998,1.1970000000000001]
[" I 0118 236 PL",49,83,98,100,42,2,36,0.59699999999999998,0.59699999999999998]
[" I 0118 255 EL",49,83,98,100,42,2,55,0.59699999999999998,0.59699999999999998]
[" I 0119 236 PL",37,67,89,100,47,2,36,0.59699999999999998,0.59699999999999998]
[" I 0119 255 EL",37,67,89,100,47,2,55,0.59699999999999998,0.59699999999999998]
[" I 0119 436",37,67,89,100,47,4,36,0.59699999999999998,1.26]
[" I 0121 218",83,100,100,100,61,2,18,0.29699999999999999,0.59699999999999998]
[" I 0121 236",83,100,100,100,61,2,36,0.29699999999999999,1.1970000000000001]
[" I 0121 258",83,100,100,100,61,2,58,0.29699999999999999,1.4970000000000001]
[" I 0121 318",81,100,100,100,67,3,18,0.59699999999999998,0.59699999999999998]
[" I 0121 336",81,100,100,100,67,3,36,0.59699999999999998,1.1970000000000001]
[" I 0121 418",81,100,100,100,67,4,18,0.59699999999999998,0.59699999999999998]
[" I 0121 436",81,100,100,100,67,4,36,0.59699999999999998,1.1970000000000001]
[" I 0122 218",90,100,100,100,57,2,18,0.29699999999999999,0.59699999999999998]
[" I 0122 236",90,100,100,100,57,2,36,0.29699999999999999,1.1970000000000001]
[" I 0122 258",90,100,100,100,57,2,58,0.29699999999999999,1.4970000000000001]
[" I 0122 318",78,100,100,100,59,3,18,0.59699999999999998,0.59699999999999998]
[" I 0122 336",78,100,100,100,59,3,36,0.59699999999999998,1.1970000000000001]
[" I 0122 418",78,100,100,100,59,4,18,0.59699999999999998,0.59699999999999998]
[" I 0122 436",78,100,100,100,59,4,36,0.59699999999999998,1.1970000000000001]
[" I 0124 218",65,95,100,100,57,2,18,0.29699999999999999,0.59699999999999998]
[" I 0124 236",65,95,100,100,57,2,36,0.29699999999999999,1.1970000000000001]
[" I 0124 258",65,95,100,100,57,2,58,0.29699999999999999,1.4970000000000001]
[" I 0124 418",70,100,100,100,64,4,18,0.59699999999999998,0.59699999999999998]
[" I 0124 436",70,100,100,100,64,4,36,0.59699999999999998,1.1970000000000001]
[" I 0125 218",70,100,100,100,42,2,18,0.29699999999999999,0.59699999999999998]
[" I 0125 236",70,100,100,100,42,2,36,0.29699999999999999,1.1970000000000001]
[" I 0125 258",70,100,100,100,42,2,58,0.29699999999999999,1.4970000000000001]
[" I 0125 418",62,94,100,100,64,4,18,0.59699999999999998,0.59699999999999998]
[" I 0125 436",62,94,100,100,64,4,36,0.59699999999999998,1.1970000000000001]
[" I 0126 218",44,76,97,100,59,2,18,0.29699999999999999,0.59699999999999998]
[" I 0126 236",44,76,97,100,59,2,36,0.29699999999999999,1.1970000000000001]
[" I 0126 258",44,76,97,100,59,2,58,0.29699999999999999,1.4970000000000001]
[" I 0126 418",44,76,97,100,59,4,18,0.59699999999999998,0.59699999999999998]
[" I 0126 436",44,76,97,100,59,4,36,0.59699999999999998,1.1970000000000001]
[" I 0127 218",51,81,98,100,58,2,18,0.29699999999999999,0.59699999999999998]
[" I 0127 236",51,81,98,100,58,2,36,0.29699999999999999,1.1970000000000001]
[" I 0127 258",51,81,98,100,58,2,58,0.29699999999999999,1.4970000000000001]
[" I 0127 418",52,82,98,100,66,4,18,0.59699999999999998,0.59699999999999998]
[" I 0127 436",52,82,98,100,66,4,36,0.59699999999999998,1.1970000000000001]
[" I 0131 218",83,100,100,100,61,2,18,0.312,0.622]
[" I 0131 236",83,100,100,100,61,2,36,0.312,1.2470000000000001]
[" I 0131 258",83,100,100,100,61,2,58,0.312,1.5469999999999999]
[" I 0131 318",81,100,100,100,67,3,18,0.622,0.622]
[" I 0131 336",81,100,100,100,67,3,36,0.622,1.2470000000000001]
[" I 0131 418",81,100,100,100,67,4,18,0.622,0.622]
[" I 0131 436",81,100,100,100,67,4,36,0.622,1.2470000000000001]
[" I 0132 218",90,100,100,100,57,2,18,0.312,0.622]
[" I 0132 236",90,100,100,100,57,2,36,0.312,1.2470000000000001]
[" I 0132 258",90,100,100,100,57,2,58,0.312,1.5469999999999999]
[" I 0132 318",78,100,100,100,59,3,18,0.622,0.622]
[" I 0132 336",78,100,100,100,59,3,36,0.622,1.2470000000000001]
[" I 0132 418",78,100,100,100,59,4,18,0.622,0.622]
[" I 0132 436",78,100,100,100,59,4,36,0.622,1.2470000000000001]
[" I 0134 218",65,95,100,100,57,2,18,0.312,0.622]
[" I 0134 236",65,95,100,100,57,2,36,0.312,1.2470000000000001]
[" I 0134 258",65,95,100,100,57,2,58,0.312,1.5469999999999999]
[" I 0134 418",70,100,100,100,64,4,18,0.622,0.622]
[" I 0134 436",70,100,100,100,64,4,36,0.622,1.2470000000000001]
[" I 0135 218",70,100,100,100,42,2,18,0.312,0.622]
[" I 0135 236",70,100,100,100,42,2,36,0.312,1.2470000000000001]
[" I 0135 258",70,100,100,100,42,2,58,0.312,1.5469999999999999]
[" I 0135 418",62,94,100,100,64,4,18,0.622,0.622]
[" I 0135 436",62,94,100,100,64,4,36,0.622,1.2470000000000001]
[" I 0136 218",44,76,97,100,59,2,18,0.312,0.622]
[" I 0136 236",44,76,97,100,59,2,36,0.312,1.2470000000000001]
[" I 0136 258",44,76,97,100,59,2,58,0.312,1.5469999999999999]
[" I 0136 418",44,76,97,100,59,4,18,0.622,0.622]
[" I 0136 436",44,76,97,100,59,4,36,0.622,1.2470000000000001]
[" I 0137 218",51,81,98,100,58,2,18,0.312,0.622]
[" I 0137 236",51,81,98,100,58,2,36,0.312,1.2470000000000001]
[" I 0137 258",51,81,98,100,58,2,58,0.312,1.5469999999999999]
[" I 0137 418",52,82,98,100,66,4,18,0.622,0.622]
[" I 0137 436",52,82,98,100,66,4,36,0.622,1.2470000000000001]
[" I 0141 118",83,100,100,100,61,1,18,0.2,0.65]
[" I 0141 136",83,100,100,100,61,1,36,0.2,1.26]
[" I 0141 158",83,100,100,100,61,1,58,0.2,1.56]
[" I 0142 118",88,100,100,100,57,1,18,0.2,0.65]
[" I 0142 136",88,100,100,100,57,1,36,0.2,1.26]
[" I 0142 158",88,100,100,100,57,1,58,0.2,1.56]
[" I 0144 118",65,95,100,100,57,1,18,0.2,0.65]
[" I 0144 136",65,95,100,100,57,1,36,0.2,1.26]
[" I 0144 158",65,95,100,100,57,1,58,0.2,1.56]
[" I 0145 118",70,100,100,100,42,1,18,0.2,0.65]
[" I 0145 136",70,100,100,100,42,1,36,0.2,1.26]
[" I 0145 158",70,100,100,100,42,1,58,0.2,1.56]
[" I 0146 118",45,76,96,100,57,1,18,0.2,0.65]
[" I 0146 136",45,76,96,100,57,1,36,0.2,1.26]
[" I 0146 158",45,76,96,100,57,1,58,0.2,1.56]
[" I 0147 118",51,81,98,100,58,1,18,0.2,0.65]
[" I 0147 136",51,81,98,100,58,1,36,0.2,1.26]
[" I 0147 158",51,81,98,100,58,1,58,0.2,1.56]
[" I 0151 118",83,100,100,100,61,1,18,0.184,0.66400000000000003]
[" I 0151 136",83,100,100,100,61,1,36,0.184,1.27]
[" I 0151 158",83,100,100,100,61,1,58,0.184,1.57]
[" I 0151 218",83,100,100,100,61,2,18,0.28399999999999997,0.66400000000000003]
[" I 0151 236",83,100,100,100,61,2,36,0.28399999999999997,1.27]
[" I 0151 258",83,100,100,100,61,2,18,0.28399999999999997,1.57]
[" I 0152 118",88,100,100,100,57,1,18,0.184,0.66400000000000003]
[" I 0152 136",88,100,100,100,57,1,36,0.184,1.27]
[" I 0152 158",88,100,100,100,57,1,58,0.184,1.57]
[" I 0152 218",88,100,100,100,57,2,18,0.28399999999999997,0.66400000000000003]
[" I 0152 236",88,100,100,100,57,2,36,0.28399999999999997,1.27]
[" I 0152 258",88,100,100,100,57,2,18,0.28399999999999997,1.57]
[" I 0154 118",65,95,100,100,57,1,18,0.184,0.66400000000000003]
[" I 0154 136",65,95,100,100,57,1,36,0.184,1.27]
[" I 0154 158",65,95,100,100,57,1,58,0.184,1.57]
[" I 0154 218",65,95,100,100,57,2,18,0.28399999999999997,0.66400000000000003]
[" I 0154 236",65,95,100,100,57,2,36,0.28399999999999997,1.27]
[" I 0154 258",65,95,100,100,57,2,18,0.28399999999999997,1.57]
[" I 0155 118",70,100,100,100,42,1,18,0.184,0.66400000000000003]
[" I 0155 136",70,100,100,100,42,1,36,0.184,1.27]
[" I 0155 158",70,100,100,100,42,1,58,0.184,1.57]
[" I 0155 218",70,100,100,100,42,2,18,0.28399999999999997,0.66400000000000003]
[" I 0155 236",70,100,100,100,42,2,36,0.28399999999999997,1.27]
[" I 0155 258",70,100,100,100,42,2,18,0.28399999999999997,1.57]
[" I 0156 118",44,76,97,100,59,1,18,0.184,0.66400000000000003]
[" I 0156 136",44,76,97,100,59,1,36,0.184,1.27]
[" I 0156 158",44,76,97,100,59,1,58,0.184,1.57]
[" I 0156 218",44,76,97,100,59,2,18,0.28399999999999997,0.66400000000000003]
[" I 0156 236",44,76,97,100,59,2,36,0.28399999999999997,1.27]
[" I 0156 258",44,76,97,100,59,2,18,0.28399999999999997,1.57]
[" I 0157 118",51,81,98,100,58,1,18,0.184,0.66400000000000003]
[" I 0157 136",51,81,98,100,58,1,36,0.184,1.27]
[" I 0157 158",51,81,98,100,58,1,58,0.184,1.57]
[" I 0157 218",51,81,98,100,58,2,18,0.28399999999999997,0.66400000000000003]
[" I 0157 236",51,81,98,100,58,2,36,0.28399999999999997,1.27]
[" I 0157 258",51,81,98,100,58,2,18,0.28399999999999997,1.57]
[" I 0211 118",83,100,100,100,61,1,18,0.185,0.64]
[" I 0211 136",83,100,100,100,61,1,36,0.185,1.25]
[" I 0211 158",83,100,100,100,61,1,58,0.185,1.55]
[" I 0211 218",83,100,100,100,61,2,18,0.28499999999999998,0.64]
[" I 0211 236",83,100,100,100,61,2,36,0.28499999999999998,1.25]
[" I 0211 258",83,100,100,100,61,2,58,0.28499999999999998,1.55]
[" I 0211 318",81,100,100,100,67,3,18,0.6,0.65]
[" I 0211 336",81,100,100,100,67,3,36,0.6,1.25]
[" I 0211 418",81,100,100,100,67,4,18,0.6,0.64]
[" I 0211 436",81,100,100,100,67,4,36,0.6,1.25]
[" I 0212 118",90,100,100,100,57,1,18,0.185,0.64]
[" I 0212 136",90,100,100,100,57,1,36,0.185,1.25]
[" I 0212 158",90,100,100,100,57,1,58,0.185,1.55]
[" I 0212 218",90,100,100,100,57,2,18,0.28499999999999998,0.64]
[" I 0212 236",90,100,100,100,57,2,36,0.28499999999999998,1.25]
[" I 0212 258",90,100,100,100,57,2,58,0.28499999999999998,1.55]
[" I 0212 318",78,100,100,100,59,3,18,0.6,0.65]
[" I 0212 336",78,100,100,100,59,3,36,0.6,1.25]
[" I 0212 418",78,100,100,100,59,4,18,0.6,0.64]
[" I 0212 436",78,100,100,100,59,4,36,0.6,1.25]
[" I 0214 118",65,95,100,100,57,1,18,0.17499999999999999,0.64]
[" I 0214 136",65,95,100,100,57,1,36,0.17499999999999999,1.25]
[" I 0214 158",65,95,100,100,57,1,58,0.17499999999999999,1.55]
[" I 0214 218",65,95,100,100,57,2,18,0.28499999999999998,0.64]
[" I 0214 236",65,95,100,100,57,2,36,0.28499999999999998,1.25]
[" I 0214 258",65,95,100,100,57,2,58,0.28499999999999998,1.55]
[" I 0214 418",70,100,100,100,64,4,18,0.6,0.64]
[" I 0214 436",70,100,100,100,64,4,36,0.6,1.25]
[" I 0215 118",70,100,100,100,42,1,18,0.17499999999999999,0.64]
[" I 0215 136",70,100,100,100,42,1,36,0.17499999999999999,1.25]
[" I 0215 158",70,100,100,100,42,1,58,0.17499999999999999,1.55]
[" I 0215 218",70,100,100,100,42,2,18,0.28499999999999998,0.64]
[" I 0215 236",70,100,100,100,42,2,36,0.28499999999999998,1.25]
[" I 0215 258",70,100,100,100,42,2,58,0.28499999999999998,1.55]
[" I 0215 418",62,94,100,100,64,4,18,0.6,0.64]
[" I 0215 436",62,94,100,100,64,4,36,0.6,1.25]
[" I 0216 118",44,76,97,100,59,1,18,0.17499999999999999,0.64]
[" I 0216 136",44,76,97,100,59,1,36,0.17499999999999999,1.25]
[" I 0216 158",44,76,97,100,59,1,58,0.17499999999999999,1.55]
[" I 0216 218",44,76,97,100,59,2,18,0.28499999999999998,0.64]
[" I 0216 236",44,76,97,100,59,2,36,0.28499999999999998,1.25]
[" I 0216 258",44,76,97,100,59,2,58,0.28499999999999998,1.55]
[" I 0216 418",44,76,97,100,59,4,18,0.6,0.64]
[" I 0216 436",44,76,97,100,59,4,36,0.6,1.25]
[" I 0217 118",51,81,98,100,58,1,18,0.17499999999999999,0.64]
[" I 0217 136",51,81,98,100,58,1,36,0.17499999999999999,1.25]
[" I 0217 158",51,81,98,100,58,1,58,0.17499999999999999,1.55]
[" I 0217 218",51,81,98,100,58,2,18,0.28499999999999998,0.64]
[" I 0217 236",51,81,98,100,58,2,36,0.28499999999999998,1.25]
[" I 0217 258",51,81,98,100,58,2,58,0.28499999999999998,1.55]
[" I 0217 418",52,82,98,100,66,4,18,0.6,0.64]
[" I 0217 436",52,82,98,100,66,4,36,0.6,1.25]
[" I 0246 118",32,60,83,67,68,1,18,0.11,0.67]
[" I 0246 136",32,60,83,67,68,1,36,0.11,1.27]
[" I 0246 218",37,66,87,73,72,2,18,0.2,0.67]
[" I 0246 236",37,66,87,73,72,2,36,0.2,1.27]
[" I 0246 258",37,66,87,73,72,2,58,0.2,1.5720000000000001]
[" I 0246 336",43,74,92,86,66,3,36,0.29699999999999999,1.27]
[" I 0246 418",43,74,92,86,66,4,18,0.66400000000000003,0.66400000000000003]
[" I 0247 118",44,71,88,75,69,1,18,0.11,0.67]
[" I 0247 136",44,71,88,75,69,1,36,0.11,1.27]
[" I 0247 218",51,83,95,93,64,2,18,0.2,0.67]
[" I 0247 236",51,83,95,93,64,2,36,0.2,1.27]
[" I 0247 258",51,83,95,93,64,2,58,0.2,1.5720000000000001]
[" I 0247 336",51,83,95,93,64,3,36,0.29699999999999999,1.27]
[" I 0247 418",51,83,95,93,64,4,18,0.66400000000000003,0.66400000000000003]
[" I 5100 118",31,59,81,66,83,1,18,0.622,0.05]
[" I 5100 136",31,59,81,66,83,1,36,1.232,0.05]
[" I 5100 158",31,59,81,66,83,1,58,1.5369999999999999,0.05]
[" I 5100 218",34,61,85,62,88,2,18,0.622,0.1]
[" I 5100 236",34,61,85,62,88,2,36,1.232,0.1]
[" I 5100 258",34,61,85,62,88,2,58,1.5369999999999999,0.1]
[" I 5101 118",47,81,97,100,71,1,18,0.622,0.11]
[" I 5101 136",47,81,97,100,71,1,36,1.232,0.11]
[" I 5101 158",47,81,97,100,71,1,58,1.5369999999999999,0.11]
[" I 5102 118",36,66,87,75,89,1,18,0.622,7.4999999999999997E-2]
[" I 5102 136",36,66,87,75,89,1,36,1.232,7.4999999999999997E-2]
[" I 5102 158",36,66,87,75,89,1,58,1.5369999999999999,7.4999999999999997E-2]
[" I 5103 136",31,59,81,66,83,1,36,1.232,0.1]
[" I 5103 158",31,59,81,66,83,1,58,1.5369999999999999,0.1]
[" I 5104 136",36,66,87,75,89,1,36,1.232,0.17]
[" I 5104 158",36,66,87,75,89,1,58,1.5369999999999999,0.17]
[" I 5201 218",46,78,96,100,76,2,18,0.622,0.17]
[" I 5201 236",46,78,96,100,76,2,36,1.232,0.17]
[" I 5201 258",46,78,96,100,76,2,58,1.5369999999999999,0.17]
[" I 5203 236",34,61,85,62,88,2,36,1.232,0.17]
[" I 5203 258",34,61,85,62,88,2,58,1.5369999999999999,0.17]
[" I 5204 236",36,66,87,75,89,2,36,1.232,0.17]
[" I 5204 258",36,66,87,75,89,2,58,1.5369999999999999,0.17]
[" I 5700 118",32,60,82,85,75,1,18,0.66400000000000003,0.10299999999999999]
[" I 5700 136",32,60,82,85,75,1,36,1.28,0.10299999999999999]
[" I 5700 158",32,60,82,85,75,1,58,1.54,0.10299999999999999]
[" I 5700 218",32,67,87,88,72,2,18,0.66400000000000003,0.16]
[" I 5700 236",32,67,87,88,72,2,36,1.28,0.16]
[" I 5700 258",32,67,87,88,72,2,58,1.54,0.16]
[" I 5800 118",32,60,82,85,75,1,18,0.67500000000000004,0.105]
[" I 5800 136",32,60,82,85,75,1,36,1.258,0.105]
[" I 5800 158",32,60,82,85,75,1,58,1.585,0.105]
[" I 5800 218",32,67,87,88,72,2,18,0.67500000000000004,0.17499999999999999]
[" I 5800 236",32,67,87,88,72,2,36,1.258,0.17499999999999999]
[" I 5800 258",32,67,87,88,72,2,58,1.585,0.17499999999999999]
[" I 5900 118",31,59,81,66,83,1,18,0.64600000000000002,6.5000000000000002E-2]
[" I 5900 136",31,59,81,66,83,1,36,1.2569999999999999,6.5000000000000002E-2]
[" I 5900 158",31,59,81,66,83,1,58,1.5569999999999999,6.5000000000000002E-2]
[" I 5900 218",34,61,85,62,88,2,18,0.64600000000000002,0.126]
[" I 5900 236",34,61,85,62,88,2,36,1.2569999999999999,0.126]
[" I 5900 258",34,61,85,62,88,2,58,1.5569999999999999,0.126]
[" I 5901 136",34,61,85,62,88,1,36,1.258,0.11]
[" I 5901 158",34,61,85,62,88,1,58,1.585,0.11]
[" I 5901 236",46,78,96,100,76,2,36,1.258,0.17]
[" I 5901 258",46,78,96,100,76,2,58,1.585,0.17]
[" I 5903 136",31,59,81,66,83,1,36,1.258,0.11]
[" I 5903 158",31,59,81,66,83,1,58,1.585,0.11]
[" I 5903 236",34,61,85,62,88,2,36,1.258,0.17]
[" I 5903 258",34,61,85,62,88,2,58,1.585,0.17]
[" I 6100 170",72,98,100,100,78,1,70,0.34,0.34]
[" I 6100 1125",72,98,100,100,78,1,125,0.34,0.34]
[" I 6200 1250",36,86,99,100,96,1,250,0.49,0.49]
[" I 6200 1400",33,80,99,100,80,1,400,0.49,0.49]
[" I 6300 1250",80,100,100,100,71,1,250,0.497,0.497]
[" I 6300 1400",51,97,100,100,71,1,400,0.497,0.497]
[]
["Philips TMS022+GMS022 1x36",37,68,92,100,82,1,36,1.23,0.18]
["Philips TMS022+GMS022 2x36",45,77,95,100,71,2,36,1.23,0.18]
["Philips TMX400+GMX465 2x36",61,91,98,100,77,2,36,1.23,0.18]